## Cover
BESS WorkBench
Sample - 4 Room UPS BESS
Design aid. Verify values against adopted codes and AHJ.
SYNTHETIC PROJECT
SYNTHETIC teaching file, not a real facility. Intentional findings: the fire area is at the 600 kWh cap (warn); gas detection is monitoring-only (hard fail) and an add-alternate; UL 9540A is missing (sprinkler sign-off blocked); relay landings are not shown; there is no high-gas signal to the FACP; setpoints are single-gas percent LEL; sensor heights are not justified; the gas panel has 4 inputs and 6 proof points, so 2 move to FACP monitor modules.

## Rooms
ID | Name | Area sf | Height ft | Wall h | Floor h | Ceiling h | Fire area | Smoke
UPS-1 | UPS BESS Room 1 | 800 | 14 | 2 | 2 | 2 | FA-1 | TRUE
UPS-2 | UPS BESS Room 2 | 800 | 14 | 2 | 2 | 2 | FA-1 | TRUE
UPS-3 | UPS BESS Room 3 | 800 | 14 | 2 | 2 | 2 | FA-1 | TRUE
UPS-4 | UPS BESS Room 4 | 800 | 14 | 2 | 2 | 2 | FA-1 | TRUE

## ESS
ID | Name | Room | Chemistry | kWh | Spacing in | UL 9540 | UL 9540A
ESS-1 | UPS string 1 | UPS-1 | lithium-ion | 150 | 36 | TRUE | FALSE
ESS-2 | UPS string 2 | UPS-2 | lithium-ion | 150 | 36 | TRUE | FALSE
ESS-3 | UPS string 3 | UPS-3 | lithium-ion | 150 | 36 | TRUE | FALSE
ESS-4 | UPS string 4 | UPS-4 | lithium-ion | 150 | 36 | TRUE | FALSE

## Fire Areas
ID | Name | Rooms | Li-ion kWh | Barrier h | Horizontal h | Separation valid | Energy status | Note
FA-1 | UPS BESS fire area | UPS-1, UPS-2, UPS-3, UPS-4 | 600 | 2 | 2 | TRUE | WARN | Single fire area. A two-hour enclosure is the room minimum; three-hour separation is only required when a split is claimed.

## Checks
Status | ID | Screen | Title | Value | Message | Citation | Edition | Tags
PASS | SCOPE-US | project | United States only | US | Jurisdiction is the United States. | BESS WorkBench scope | WorkBench
PASS | CODE-EDITION | project | Recorded code editions | 1.0.0 | Recorded editions match the rules file ifc 2024, ibc 2024, imc 2024, nec 2023, nfpa_855 2023, nfpa_72 2022, nfpa_13 2025, nfpa_69 2024. Ruleset ifc2024_nfpa855_2023 1.0.0. NEC is recorded only; this workbook does not size conductors. | Project code basis | WorkBench
PASS | FP-ROOM-2H | rooms | Two-hour room enclosure | 2 h | In-scope room walls are at least 2 h. | IFC 2024 1207.7.4 | IFC 2024 | CODE
PASS | FP-UL9540 | rooms | UL 9540 listing | listed | In-scope groups are recorded as UL 9540 listed. | IFC 2024 1207.3.1 | IFC 2024 | CODE
PASS | FP-SPACING | rooms | Array spacing record | UPS string 1 36 in, UPS string 2 36 in, UPS string 3 36 in, UPS string 4 36 in | Spacing on file: UPS string 1 36 in, UPS string 2 36 in, UPS string 3 36 in, UPS string 4 36 in. | Project record | WorkBench
PASS | FP-CHEM-OTHER | rooms | Chemistry outside the lithium-ion row | lithium-ion | Every group with energy is in the lithium-ion family. | IFC 2024 Table 1207.1.1 | IFC 2024
PASS | FA-SMOKE | rooms | Smoke detection in each BESS room | smoke | Smoke detection is recorded in each in-scope room. | IFC 2024 1207.5.4 | IFC 2024 | ASSUMED, CODE
PASS | FP-THRESH-20 | thresholds | Lithium-ion room threshold | 20 kWh/room | ESS room rules apply to every room at or above the threshold. UPS BESS Room 1: 150 kWh at or above 20 kWh; UPS BESS Room 2: 150 kWh at or above 20 kWh; UPS BESS Room 3: 150 kWh at or above 20 kWh; UPS BESS Room 4: 150 kWh at or above 20 kWh. | IFC 2024 Table 1207.1.1 | IFC 2024 | CODE
PASS | FP-FA-SEP | thresholds | Two-hour rooms combine; three-hour barriers separate | 1 claimed fire area(s) | No split is claimed, so two-hour rooms stay one combined fire area. | IBC 2024 Table 707.3.10 | IBC 2024 | ASSUMED
WARN | FP-FA-600 | thresholds | Energy per fire area | 600 kWh | FA-1: 600 kWh lithium-ion (WARN; warn band 570–600 kWh) | IFC 2024 Table 1207.5 | IFC 2024 | ASSUMED
PASS | FP-IMC-FSD | explosion | No fire or smoke damper on gas exhaust | clear | No fire damper and no smoke damper on the gas exhaust. | IMC 2024 509.6.1 | IMC 2024 | CODE
PASS | FP-IMC-BAL | explosion | No balancing damper on gas exhaust | clear | No balancing damper on the gas exhaust. | IMC 2024 509.5.1 | IMC 2024 | CODE
PASS | FP-IMC-BD | explosion | No backdraft damper on gas exhaust | clear | No backdraft damper on the gas exhaust. | IMC 2024 509 | IMC 2024 | CODE
PASS | FP-IMC-SHAFT | explosion | Rated shaft for the gas exhaust | shaft | A rated shaft is indicated where the duct crosses a rated assembly. | IMC 2024 509.6.1.1 | IMC 2024 | CODE
PASS | FP-IMC-MOTOR | explosion | Motorized damper fail-open and proven open | motorized damper | Motorized damper fails open and proves open to the FACP. | FP lead 2026-10-21 | FP lead 2026-10-21 | CODE
PASS | FP-IMC-OTHER | explosion | Dampers in other ducts through BESS walls | none | No other ducts are flagged through BESS walls. | IBC 2024 Table 717.3.2.1 | IBC 2024 | CODE
PASS | FA-IMC-509 | explosion | Gas exhaust duct constraints | PASS | The IMC duct line items pass, which is also FA lead item 10. | IMC 2024 509 | IMC 2024 | ASSUMED
PASS | FP-EXH-LOGIC | explosion | Low alarm starts exhaust and makeup | latched | Low alarm from either gas starts exhaust and makeup air, latched, with manual reset. | FP lead 2026-10-21 | FP lead 2026-10-21 | CODE
PASS | FA-NO-SHUTDOWN | explosion | Fire alarm does not stop gas exhaust | exhaust stays on | HVAC shutdown is not marked as stopping the gas exhaust. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
PASS | FA-EXH-STANDBY | explosion | Exhaust fan standby power | 2 h | Standby power is indicated for the exhaust fan (2 h per the rules file). Verify IFC 1207.6.1.2 and NFPA 855 before issuing. | IFC 2024 1207.6.1.2 | IFC 2024 | ASSUMED, NEEDS PE REVIEW
PASS | FP-LFL-10 | explosion | Low-alarm setpoint | 10% | Low-alarm setpoint is 10% LFL (limit 10%). Subsection 9.6.5.6 still needs PE review. | NFPA 855-2023 9.6.5.6 | NFPA 855-2023 | CODE, ASSUMED, NEEDS PE REVIEW
WARN | FP-LFL-25 | explosion | Design LFL fraction | 25% | Design fraction is exactly 25% LFL. The FP lead states 25 percent and the FA lead states below 25 percent. A PE has to close that conflict. | NFPA 855-2023 9.6.5.6 | NFPA 855-2023 | ASSUMED, NEEDS PE REVIEW
INFO | GAS-MB | explosion | Release mass-balance helper | no data | No release mass and room volume are entered, so the helper has nothing to compute. | Ideal-gas helper at 70 F and 1 atm | WorkBench | ASSUMED
INFO | FA-SETPOINT-CONV | explosion | Setpoint conversion | no data | No release case is available to convert into a mixture percent LFL. | NFPA 855-2023 9.6.5.6 | NFPA 855-2023 | ASSUMED, NEEDS PE REVIEW
PASS | FP-SENSOR-COVER | gas | One sensor per listed gas per room | H2, DMC | Each room has a sensor for every gas on the default H2 and DMC list. | IFC 2024 916.3 | IFC 2024 | CODE, ASSUMED
WARN | FP-LFL-SINGLE | gas | Single-gas percent LEL | single_gas_lel | Setpoints are single-gas percent LEL and UL 9540A gas data is not on file. That is not a vent-gas mixture setpoint. | NFPA 855-2023 9.6.5.6 | NFPA 855-2023 | ASSUMED, NEEDS PE REVIEW
FAIL | FA-HARD-MON | gas | Monitoring-only or BACnet-only gas detection | monitoring-only | Hard fail: gas detection is monitoring-only while it is the explosion control. The life-safety sequence has to be hardwired. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
PASS | FA-HARD-NAC | gas | Gas horns are not on fire-alarm NACs | separate | Gas horns are not on fire-alarm NACs. | IFC 2024 916.8 | IFC 2024 | ASSUMED, CODE
PASS | FA-DISTINCT | gas | Gas notification distinct from fire alarm | distinct | Gas notification is marked distinct from the fire alarm. | IFC 2024 916.8 | IFC 2024 | ASSUMED, CODE
PASS | FA-RELAYS | gas | Relay map R1, R2, R3, and fault | R1/R2/R3/fault | Relay map covers R1, R2, R3, and the fault relay. R1=Exhaust and makeup, latched, manual reset, R2=Gas alarm to FACP, R3=Gas horns and strobes, R4=Spare, FAULT=Trouble to FACP. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
PASS | FA-H2-CEILING | gas | Hydrogen sensor near the ceiling | <= 12 in | Hydrogen sensors are high and within 12 in of the ceiling. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
PASS | FA-DMC-LOW | gas | DMC sensor low | low | DMC sensors are mounted low. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
WARN | FA-HEIGHT-OPEN | gas | Sensor height still an open item | 8 open | Height is still an open item for UPS-1-H2, UPS-1-DMC, UPS-2-H2, UPS-2-DMC, UPS-3-H2, UPS-3-DMC, UPS-4-H2, UPS-4-DMC. Justify each one from UL 9540A data and airflow with exhaust on and with exhaust failed. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
WARN | FA-PROOFS | gas | Proof points and input shortfall | 2 on FACP | 6 proof points and 4 gas-panel inputs. 2 proof point(s) move to FACP monitor modules. Loss of proof is supervisory. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
PASS | FA-SUPERVISING | gas | Signals to the supervising station | yes | Gas alarm, trouble, and supervisory are marked for transmission to the supervising station. | NFPA 72-2022 supervising station | NFPA 72-2022 | ASSUMED
WARN | FP-LAND-RFI | gas | Relay landings not shown | not shown | Relay landings for R1, R2, R3, and the fault relay are not shown. | FP lead 2026-10-21 | FP lead 2026-10-21
WARN | FP-HIGH-RFI | gas | High-gas signal to the FACP | no | No high-gas signal to the FACP is indicated. Local horns are not that signal. | FP lead 2026-10-21 | FP lead 2026-10-21
PASS | CE-STOP | cause_effect | Cause and effect does not stop exhaust | exhaust stays on | No matrix row stops the gas exhaust. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
PASS | CE-SOURCE | cause_effect | Cause and effect source | generated | The matrix is generated from the lead sequence and refreshes until someone edits a cell. | BESS WorkBench | WorkBench
PASS | FP-SPR-TYPE | sprinklers | Sprinkler system type | wet | System type is wet. | BESS WorkBench scope | WorkBench
PASS | FP-SPR-DESIGN | sprinklers | Density times design area | 240.00 gpm | design area = min(room, 2500 sf) x 1; sprinkler gpm = 0.3 gpm/sf x design area; worksheet total = governing 240.00 gpm + hose 100.00 gpm. Governing room UPS-1. | IFC 2024 1207.5.5 | IFC 2024 | CODE
PASS | FP-SPR-30 | sprinklers | Dry and double-interlock area increase | delta 0 sf | Wet system: the dry/preaction area increase is not applied. Delta is 0 sf. | NFPA 13-2025 19.2.3.2.5 | NFPA 13-2025 | ASSUMED
BLOCKED | FP-SPR-9540A | sprinklers | Sprinkler sign-off blocked without UL 9540A | UPS string 1, UPS string 2, UPS string 3, UPS string 4 | Sprinkler sign-off is blocked. Groups above 50 kWh without a UL 9540A report: UPS string 1, UPS string 2, UPS string 3, UPS string 4. The density math is still shown. | BESS WorkBench scope rule | WorkBench | ASSUMED
PASS | FP-SPR-C100 | sprinklers | Hazen-Williams C | C=100 | Hazen-Williams C is fixed at 100. This is a recorded basis, not a hydraulic model. | FP lead 2026-10-21 | NFPA 13-2025 | ASSUMED
PASS | FP-SPR-HOSE | sprinklers | Hose allowance | 100 gpm / 60 min | Hose 100 gpm for 60 min. Worksheet volume 20400 gal (governing sprinkler demand plus hose). | FP lead 2026-10-21 | FP lead 2026-10-21 | ASSUMED
PASS | FP-SPR-DUCT | sprinklers | Duct sprinkler flow | 14.82 gpm | q = K * sqrt(p) = 5.60 * sqrt(7.00) = 14.82 gpm | NFPA 13-2025 minimum sprinkler pressure | NFPA 13-2025 | ASSUMED
WARN | FP-9540A-RFI | sprinklers | UL 9540A report missing | UPS string 1 (150 kWh), UPS string 2 (150 kWh), UPS string 3 (150 kWh), UPS string 4 (150 kWh) | UL 9540A report is not on file for UPS string 1 (150 kWh), UPS string 2 (150 kWh), UPS string 3 (150 kWh), UPS string 4 (150 kWh). | FP lead 2026-10-21 | FP lead 2026-10-21
PASS | FA-BATT-FACP | battery | FACP battery duration | 20.07 Ah | FACP worksheet is 24 h standby + 5 min (5 min alarm). (0.50 A x 24.00 h) + (2.00 A x 0.08 h) = 12.17 Ah; x 1.20 margin x 1.25 aging x 1.10 temp = 20.07 Ah. Next standard size: 26.0 Ah. | NFPA 72-2022 10.6.7.2 | NFPA 72-2022 | ASSUMED, CODE
PASS | FA-BATT-GAS | battery | Gas panel battery duration | 12.54 Ah | Gas panel worksheet is 24 h standby + 2 h alarm. (0.25 A x 24.00 h) + (0.80 A x 2.00 h) = 7.60 Ah; x 1.20 margin x 1.25 aging x 1.10 temp = 12.54 Ah. Next standard size: 18.0 Ah. Verify IFC 1207.6.1.2 and NFPA 855. | IFC 2024 1207.6.1.2 | IFC 2024 | ASSUMED, NEEDS PE REVIEW
PASS | FA-BATT-MARGIN | battery | Battery margin and derate | 20% | Margin 20%, aging x1.25, temperature x1.10. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED
WARN | FA-DOOR | rfi | Door hardware follows the barrier | open coordination item | Confirm door and frame ratings match the barrier (2 h door in a 2 h wall, 3 h door in a 3 h wall) and that hold-open devices release on a fire-alarm signal. | FA lead 2026-10-21 | FA lead 2026-10-21 | ASSUMED

## Points
Point | Description | Kind | Landing | Normal | Off-normal
UPS-1-H2 | H2 sensor in UPS-1 | sensor | Gas panel sensor channel UPS-1-H2 | Normal | Low alarm / high alarm / fault
UPS-1-DMC | DMC sensor in UPS-1 | sensor | Gas panel sensor channel UPS-1-DMC | Normal | Low alarm / high alarm / fault
UPS-2-H2 | H2 sensor in UPS-2 | sensor | Gas panel sensor channel UPS-2-H2 | Normal | Low alarm / high alarm / fault
UPS-2-DMC | DMC sensor in UPS-2 | sensor | Gas panel sensor channel UPS-2-DMC | Normal | Low alarm / high alarm / fault
UPS-3-H2 | H2 sensor in UPS-3 | sensor | Gas panel sensor channel UPS-3-H2 | Normal | Low alarm / high alarm / fault
UPS-3-DMC | DMC sensor in UPS-3 | sensor | Gas panel sensor channel UPS-3-DMC | Normal | Low alarm / high alarm / fault
UPS-4-H2 | H2 sensor in UPS-4 | sensor | Gas panel sensor channel UPS-4-H2 | Normal | Low alarm / high alarm / fault
UPS-4-DMC | DMC sensor in UPS-4 | sensor | Gas panel sensor channel UPS-4-DMC | Normal | Low alarm / high alarm / fault
R1 | Exhaust and makeup, latched, manual reset | relay | R1 | De-energized | Energized on the mapped cause
R2 | Gas alarm to FACP | relay | R2 | De-energized | Energized on the mapped cause
R3 | Gas horns and strobes | relay | R3 | De-energized | Energized on the mapped cause
R4 | Spare | relay | R4 | De-energized | Energized on the mapped cause
FAULT | Trouble to FACP | relay | FAULT | Normal | Trouble to FACP
P1 | Exhaust fan proof | proof | Gas panel IN1 | Proved | Supervisory on loss of proof
P2 | Makeup air proof | proof | Gas panel IN2 | Proved | Supervisory on loss of proof
P3 | Damper proven open — UPS BESS Room 1 | proof | Gas panel IN3 | Proved | Supervisory on loss of proof
P4 | Damper proven open — UPS BESS Room 2 | proof | Gas panel IN4 | Proved | Supervisory on loss of proof
P5 | Damper proven open — UPS BESS Room 3 | proof | FACP monitor module MM1 | Proved | Supervisory on loss of proof
P6 | Damper proven open — UPS BESS Room 4 | proof | FACP monitor module MM2 | Proved | Supervisory on loss of proof

## Cause and Effect
Cause | Start exhaust | Start makeup air | Latch, manual reset | Gas alarm to FACP | Gas horns and strobes | Trouble to FACP | Supervisory to FACP | Release door hold-opens | Keep exhaust running | Stop exhaust | Notes
Low gas alarm (H2 or DMC) | X | X | X | X |  |  |  |  | X |  | Either gas. Latched. Manual reset at the gas panel. Does not use fire-alarm NACs.
High gas alarm (H2 or DMC) | X | X | X | X | X |  |  |  | X |  | Horns and strobes are the gas system, distinct from the fire alarm.
Gas detector fault | [5 empty] | X |  |  | X |  | Fault relay to FACP as trouble.
Exhaust fan proof loss | [6 empty] | X |  | X |  | Supervisory. Do not stop the remaining exhaust path.
Makeup air proof loss | [6 empty] | X |  | X |  | Supervisory.
Damper not proven open | [6 empty] | X |  | X |  | Supervisory. Damper is fail-open.
Smoke / fire alarm in the BESS room | [7 empty] | X | X |  | Releases door hold-opens. Does not stop gas exhaust.
Manual reset | [10 empty] | Clears the latch only after the gas condition is clear. Reset does not itself stop a running fan.

## Sprinklers
Room | Area sf | Base sf | Increase sf | Design sf | Density | gpm | Governing
UPS BESS Room 1 | 800 | 800 | 0 | 800 | 0.3 | 240 | TRUE
UPS BESS Room 2 | 800 | 800 | 0 | 800 | 0.3 | 240 | FALSE
UPS BESS Room 3 | 800 | 800 | 0 | 800 | 0.3 | 240 | FALSE
UPS BESS Room 4 | 800 | 800 | 0 | 800 | 0.3 | 240 | FALSE

## Battery
Name | Raw Ah | Margin | Aging | Temp | Required Ah | Next standard Ah | Formula
FACP | 12.1667 | 0.2 | 1.25 | 1.1 | 20.075 | 26 | (0.50 A x 24.00 h) + (2.00 A x 0.08 h) = 12.17 Ah; x 1.20 margin x 1.25 aging x 1.10 temp = 20.07 Ah
Gas panel | 7.6 | 0.2 | 1.25 | 1.1 | 12.54 | 18 | (0.25 A x 24.00 h) + (0.80 A x 2.00 h) = 7.60 Ah; x 1.20 margin x 1.25 aging x 1.10 temp = 12.54 Ah

## RFIs
ID | Status | Source | Assignee | Due | Rule | Title | Text | AI drafted
RFI-001 | open | auto | Controls vendor |  | FA-PROOFS | Proof points and input shortfall | WARN: 6 proof points and 4 gas-panel inputs. 2 proof point(s) move to FACP monitor modules. Loss of proof is supervisory. | FALSE
RFI-002 | open | auto | Mech |  | FA-SETPOINT-CONV | Setpoint conversion | INFO: No release case is available to convert into a mixture percent LFL. | FALSE
RFI-003 | open | auto | Owner |  | FP-FA-600 | Energy per fire area | WARN: FA-1: 600 kWh lithium-ion (WARN; warn band 570–600 kWh) | FALSE
RFI-004 | open | auto | Mech |  | FP-LFL-25 | Design LFL fraction | WARN: Design fraction is exactly 25% LFL. The FP lead states 25 percent and the FA lead states below 25 percent. A PE has to close that conflict. | FALSE
RFI-005 | open | auto | Owner |  | FP-SPR-9540A | Sprinkler sign-off blocked without UL 9540A | BLOCKED: Sprinkler sign-off is blocked. Groups above 50 kWh without a UL 9540A report: UPS string 1, UPS string 2, UPS string 3, UPS string 4. The density math is still shown. | FALSE
RFI-006 | open | auto | Mech |  | GAS-MB | Release mass-balance helper | INFO: No release mass and room volume are entered, so the helper has nothing to compute. | FALSE
RFI-007 | open | auto | Owner |  | FP-9540A-RFI | UL 9540A report missing | Provide the UL 9540A report for UPS string 1, UPS string 2, UPS string 3, UPS string 4. Sprinkler density cannot be reduced without it, and groups above the workbench cutoff block sprinkler sign-off. | FALSE
RFI-008 | open | auto | Architect |  | FA-DOOR | Door hardware follows the barrier | Confirm door and frame ratings match the barrier (2 h door in a 2 h wall, 3 h door in a 3 h wall) and that hold-open devices release on a fire-alarm signal. | FALSE
RFI-009 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-1-DMC in UPS-1 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-010 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-1-H2 in UPS-1 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-011 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-2-DMC in UPS-2 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-012 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-2-H2 in UPS-2 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-013 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-3-DMC in UPS-3 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-014 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-3-H2 in UPS-3 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-015 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-4-DMC in UPS-4 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-016 | open | auto | Controls vendor |  | FA-HEIGHT-OPEN | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-4-H2 in UPS-4 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. | FALSE
RFI-017 | open | auto | Elec |  | FP-HIGH-RFI | High-gas signal to the FACP | Provide a high-gas signal to the FACP. Local horns and strobes do not replace that signal. | FALSE
RFI-018 | open | auto | Controls vendor |  | FP-LAND-RFI | Relay landings not shown | Show relay landings for R1 (exhaust and makeup), R2 (gas alarm to the FACP), R3 (gas horns and strobes), and the fault relay (trouble to the FACP). | FALSE
RFI-019 | open | auto | Controls vendor |  | FA-HARD-MON | Monitoring-only or BACnet-only gas detection | Gas detection is marked as monitoring-only and an add-alternate. Confirm it is base-scope, hardwired explosion control and not a monitoring-only or add-alternate system. | FALSE
RFI-020 | open | auto | Controls vendor |  | FP-LFL-SINGLE | Single-gas percent LEL | Setpoints are single-gas percent LEL and UL 9540A gas data is not on file. That is not a vent-gas mixture setpoint. Provide UL 9540A gas species and volumes, or a mixture setpoint a PE will accept. | FALSE