# Basis of Design

Sample - 4 Room UPS BESS

SYNTHETIC PROJECT — not a real facility.

Design aid. Verify values against adopted codes and AHJ.

# Project

| Field | Value |
| --- | --- |
| Project number | SYN-DC-001 |
| Client | Synthetic Hyperscale (not a real owner) |
| Site | Synthetic campus, United States |
| Prepared by | BESS WorkBench sample |
| Ruleset | ifc2024_nfpa855_2023 1.0.0 |
| Occupancy | F-1 |
| Jurisdiction | US |

SYNTHETIC teaching file, not a real facility. Intentional findings: the fire area is at the 600 kWh cap (warn); gas detection is monitoring-only (hard fail) and an add-alternate; UL 9540A is missing (sprinkler sign-off blocked); relay landings are not shown; there is no high-gas signal to the FACP; setpoints are single-gas percent LEL; sensor heights are not justified; the gas panel has 4 inputs and 6 proof points, so 2 move to FACP monitor modules.

# Code basis

| Document | Edition |
| --- | --- |
| IFC | 2024 |
| IBC | 2024 |
| IMC | 2024 |
| NEC | 2023 |
| NFPA 855 | 2023 |
| NFPA 72 | 2022 |
| NFPA 13 | 2025 |
| NFPA 69 | 2024 |

AHJ notes: SYNTHETIC AHJ. No authority has reviewed this file.

# Narrative

No AI narrative has been drafted.

# Rooms

| Room | Area sf | Height ft | Wall h | Floor h | Ceiling h | Fire area | Smoke |
| --- | --- | --- | --- | --- | --- | --- | --- |
| UPS BESS Room 1 | 800 | 14 | 2 | 2 | 2 | FA-1 | yes |
| UPS BESS Room 2 | 800 | 14 | 2 | 2 | 2 | FA-1 | yes |
| UPS BESS Room 3 | 800 | 14 | 2 | 2 | 2 | FA-1 | yes |
| UPS BESS Room 4 | 800 | 14 | 2 | 2 | 2 | FA-1 | yes |

# ESS inventory

| Group | Room | Chemistry | kWh | Spacing in | UL 9540 | UL 9540A |
| --- | --- | --- | --- | --- | --- | --- |
| UPS string 1 | UPS-1 | lithium-ion | 150 | 36 | yes | no |
| UPS string 2 | UPS-2 | lithium-ion | 150 | 36 | yes | no |
| UPS string 3 | UPS-3 | lithium-ion | 150 | 36 | yes | no |
| UPS string 4 | UPS-4 | lithium-ion | 150 | 36 | yes | no |

# Fire areas

| Fire area | kWh | Barrier h | Floor/ceiling h | Separation | Energy |
| --- | --- | --- | --- | --- | --- |
| FA-1 | 600 | 2 | 2 | yes | WARN |

# Sprinklers

design area = min(room, 2500 sf) x 1; sprinkler gpm = 0.3 gpm/sf x design area; worksheet total = governing 240.00 gpm + hose 100.00 gpm

System wet. Governing UPS-1: 240.00 gpm sprinkler + 100.00 gpm hose = 340.00 gpm for 60 min (20400 gal worksheet). C=100.

Duct sprinkler: q = K * sqrt(p) = 5.60 * sqrt(7.00) = 14.82 gpm

# Gas detection

Monitoring-only: yes. Add alternate: yes. Alarm 10% LFL. Design 25% LFL. Proof points: 6, on the gas panel 4, on FACP modules 2.

# Batteries

FACP: (0.50 A x 24.00 h) + (2.00 A x 0.08 h) = 12.17 Ah; x 1.20 margin x 1.25 aging x 1.10 temp = 20.07 Ah

Gas panel: (0.25 A x 24.00 h) + (0.80 A x 2.00 h) = 7.60 Ah; x 1.20 margin x 1.25 aging x 1.10 temp = 12.54 Ah

# Open items

| ID | Status | Assignee | Title | Text |
| --- | --- | --- | --- | --- |
| RFI-001 | open | Controls vendor | Proof points and input shortfall | WARN: 6 proof points and 4 gas-panel inputs. 2 proof point(s) move to FACP monitor modules. Loss of proof is supervisory. |
| RFI-002 | open | Mech | Setpoint conversion | INFO: No release case is available to convert into a mixture percent LFL. |
| RFI-003 | open | Owner | Energy per fire area | WARN: FA-1: 600 kWh lithium-ion (WARN; warn band 570–600 kWh) |
| RFI-004 | open | Mech | Design LFL fraction | WARN: Design fraction is exactly 25% LFL. The FP lead states 25 percent and the FA lead states below 25 percent. A PE has to close that conflict. |
| RFI-005 | open | Owner | Sprinkler sign-off blocked without UL 9540A | BLOCKED: Sprinkler sign-off is blocked. Groups above 50 kWh without a UL 9540A report: UPS string 1, UPS string 2, UPS string 3, UPS string 4. The density math is still shown. |
| RFI-006 | open | Mech | Release mass-balance helper | INFO: No release mass and room volume are entered, so the helper has nothing to compute. |
| RFI-007 | open | Owner | UL 9540A report missing | Provide the UL 9540A report for UPS string 1, UPS string 2, UPS string 3, UPS string 4. Sprinkler density cannot be reduced without it, and groups above the workbench cutoff block sprinkler sign-off. |
| RFI-008 | open | Architect | Door hardware follows the barrier | Confirm door and frame ratings match the barrier (2 h door in a 2 h wall, 3 h door in a 3 h wall) and that hold-open devices release on a fire-alarm signal. |
| RFI-009 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-1-DMC in UPS-1 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-010 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-1-H2 in UPS-1 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-011 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-2-DMC in UPS-2 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-012 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-2-H2 in UPS-2 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-013 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-3-DMC in UPS-3 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-014 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-3-H2 in UPS-3 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-015 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of DMC sensor UPS-4-DMC in UPS-4 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-016 | open | Controls vendor | Sensor height still an open item | Justify the mounting height of H2 sensor UPS-4-H2 in UPS-4 from the UL 9540A gas data and the airflow with exhaust on and with exhaust failed. |
| RFI-017 | open | Elec | High-gas signal to the FACP | Provide a high-gas signal to the FACP. Local horns and strobes do not replace that signal. |
| RFI-018 | open | Controls vendor | Relay landings not shown | Show relay landings for R1 (exhaust and makeup), R2 (gas alarm to the FACP), R3 (gas horns and strobes), and the fault relay (trouble to the FACP). |
| RFI-019 | open | Controls vendor | Monitoring-only or BACnet-only gas detection | Gas detection is marked as monitoring-only and an add-alternate. Confirm it is base-scope, hardwired explosion control and not a monitoring-only or add-alternate system. |
| RFI-020 | open | Controls vendor | Single-gas percent LEL | Setpoints are single-gas percent LEL and UL 9540A gas data is not on file. That is not a vent-gas mixture setpoint. Provide UL 9540A gas species and volumes, or a mixture setpoint a PE will accept. |

# Checks

| Status | ID | Value | Citation | Tags |
| --- | --- | --- | --- | --- |
| PASS | SCOPE-US | US | BESS WorkBench scope |  |
| PASS | CODE-EDITION | 1.0.0 | Project code basis |  |
| PASS | FP-ROOM-2H | 2 h | IFC 2024 1207.7.4 | CODE |
| PASS | FP-UL9540 | listed | IFC 2024 1207.3.1 | CODE |
| PASS | FP-SPACING | UPS string 1 36 in, UPS string 2 36 in, UPS string 3 36 in, UPS string 4 36 in | Project record |  |
| PASS | FP-CHEM-OTHER | lithium-ion | IFC 2024 Table 1207.1.1 |  |
| PASS | FA-SMOKE | smoke | IFC 2024 1207.5.4 | ASSUMED, CODE |
| PASS | FP-THRESH-20 | 20 kWh/room | IFC 2024 Table 1207.1.1 | CODE |
| PASS | FP-FA-SEP | 1 claimed fire area(s) | IBC 2024 Table 707.3.10 | ASSUMED |
| WARN | FP-FA-600 | 600 kWh | IFC 2024 Table 1207.5 | ASSUMED |
| PASS | FP-IMC-FSD | clear | IMC 2024 509.6.1 | CODE |
| PASS | FP-IMC-BAL | clear | IMC 2024 509.5.1 | CODE |
| PASS | FP-IMC-BD | clear | IMC 2024 509 | CODE |
| PASS | FP-IMC-SHAFT | shaft | IMC 2024 509.6.1.1 | CODE |
| PASS | FP-IMC-MOTOR | motorized damper | FP lead 2026-10-21 | CODE |
| PASS | FP-IMC-OTHER | none | IBC 2024 Table 717.3.2.1 | CODE |
| PASS | FA-IMC-509 | PASS | IMC 2024 509 | ASSUMED |
| PASS | FP-EXH-LOGIC | latched | FP lead 2026-10-21 | CODE |
| PASS | FA-NO-SHUTDOWN | exhaust stays on | FA lead 2026-10-21 | ASSUMED |
| PASS | FA-EXH-STANDBY | 2 h | IFC 2024 1207.6.1.2 | ASSUMED, NEEDS PE REVIEW |
| PASS | FP-LFL-10 | 10% | NFPA 855-2023 9.6.5.6 | CODE, ASSUMED, NEEDS PE REVIEW |
| WARN | FP-LFL-25 | 25% | NFPA 855-2023 9.6.5.6 | ASSUMED, NEEDS PE REVIEW |
| INFO | GAS-MB | no data | Ideal-gas helper at 70 F and 1 atm | ASSUMED |
| INFO | FA-SETPOINT-CONV | no data | NFPA 855-2023 9.6.5.6 | ASSUMED, NEEDS PE REVIEW |
| PASS | FP-SENSOR-COVER | H2, DMC | IFC 2024 916.3 | CODE, ASSUMED |
| WARN | FP-LFL-SINGLE | single_gas_lel | NFPA 855-2023 9.6.5.6 | ASSUMED, NEEDS PE REVIEW |
| FAIL | FA-HARD-MON | monitoring-only | FA lead 2026-10-21 | ASSUMED |
| PASS | FA-HARD-NAC | separate | IFC 2024 916.8 | ASSUMED, CODE |
| PASS | FA-DISTINCT | distinct | IFC 2024 916.8 | ASSUMED, CODE |
| PASS | FA-RELAYS | R1/R2/R3/fault | FA lead 2026-10-21 | ASSUMED |
| PASS | FA-H2-CEILING | <= 12 in | FA lead 2026-10-21 | ASSUMED |
| PASS | FA-DMC-LOW | low | FA lead 2026-10-21 | ASSUMED |
| WARN | FA-HEIGHT-OPEN | 8 open | FA lead 2026-10-21 | ASSUMED |
| WARN | FA-PROOFS | 2 on FACP | FA lead 2026-10-21 | ASSUMED |
| PASS | FA-SUPERVISING | yes | NFPA 72-2022 supervising station | ASSUMED |
| WARN | FP-LAND-RFI | not shown | FP lead 2026-10-21 |  |
| WARN | FP-HIGH-RFI | no | FP lead 2026-10-21 |  |
| PASS | CE-STOP | exhaust stays on | FA lead 2026-10-21 | ASSUMED |
| PASS | CE-SOURCE | generated | BESS WorkBench |  |
| PASS | FP-SPR-TYPE | wet | BESS WorkBench scope |  |
| PASS | FP-SPR-DESIGN | 240.00 gpm | IFC 2024 1207.5.5 | CODE |
| PASS | FP-SPR-30 | delta 0 sf | NFPA 13-2025 19.2.3.2.5 | ASSUMED |
| BLOCKED | FP-SPR-9540A | UPS string 1, UPS string 2, UPS string 3, UPS string 4 | BESS WorkBench scope rule | ASSUMED |
| PASS | FP-SPR-C100 | C=100 | FP lead 2026-10-21 | ASSUMED |
| PASS | FP-SPR-HOSE | 100 gpm / 60 min | FP lead 2026-10-21 | ASSUMED |
| PASS | FP-SPR-DUCT | 14.82 gpm | NFPA 13-2025 minimum sprinkler pressure | ASSUMED |
| WARN | FP-9540A-RFI | UPS string 1 (150 kWh), UPS string 2 (150 kWh), UPS string 3 (150 kWh), UPS string 4 (150 kWh) | FP lead 2026-10-21 |  |
| PASS | FA-BATT-FACP | 20.07 Ah | NFPA 72-2022 10.6.7.2 | ASSUMED, CODE |
| PASS | FA-BATT-GAS | 12.54 Ah | IFC 2024 1207.6.1.2 | ASSUMED, NEEDS PE REVIEW |
| PASS | FA-BATT-MARGIN | 20% | FA lead 2026-10-21 | ASSUMED |
| WARN | FA-DOOR | open coordination item | FA lead 2026-10-21 | ASSUMED |