## Cause and Effect
Cause | Start exhaust | Start makeup air | Latch, manual reset | Gas alarm to FACP | Gas horns and strobes | Trouble to FACP | Supervisory to FACP | Release door hold-opens | Keep exhaust running | Stop exhaust | Notes
Low gas alarm (H2 or DMC) | X | X | X | X |  |  |  |  | X |  | Either gas. Latched. Manual reset at the gas panel. Does not use fire-alarm NACs.
High gas alarm (H2 or DMC) | X | X | X | X | X |  |  |  | X |  | Horns and strobes are the gas system, distinct from the fire alarm.
Gas detector fault | [5 empty] | X |  |  | X |  | Fault relay to FACP as trouble.
Exhaust fan proof loss | [6 empty] | X |  | X |  | Supervisory. Do not stop the remaining exhaust path.
Makeup air proof loss | [6 empty] | X |  | X |  | Supervisory.
Damper not proven open | [6 empty] | X |  | X |  | Supervisory. Damper is fail-open.
Smoke / fire alarm in the BESS room | [7 empty] | X | X |  | Releases door hold-opens. Does not stop gas exhaust.
Manual reset | [10 empty] | Clears the latch only after the gas condition is clear. Reset does not itself stop a running fan.